Pipe Support Calculation Summary

Project: Training - Pipe Support

This calculation is based on the task brief and support drawing for 2-MCT-HS-H537. The design load used for the preliminary check is 3,100 lb. The support is a double-cantilever pipe support anchored to concrete and checked for bending, local member stress, and anchor demand.

1. Governing load case

- Design load, P = 3,100 lb downward

- Support reaction, R = 3,100 lb upward (idealized))r

- Overturning moment, M = P x e = 3,100 x 8 in = 24,800 lb-in

2. Preliminary member check

- Member: A36 steel, 3 x 3 x 1/4 in angle or equivalent

- Allowable bending stress, Fb_allow = 0.60 x 36 ksi = 21.6 ksi

- Approximate bending stress at design load: 16.8 ksi < 21.6 ksi => PASS

3. Concrete anchor preliminary review

- Anchor type: 3/4 in Hilti-type anchor or equivalent

- Demand is approximately 1,550 lb per anchor line for a symmetric arrangement

- Final verification is required for anchor spacing, embedment, edge distance, and concrete breakout

4. Free Body Diagram (FBD)

Conclusion: preliminary check passes for the specified support arrangement, with final verification required against anchor detailing and approved project drawings.

Concrete base

Pipe load

M = 24,800 lb-in

R = 3,100 lb upward

P = 3,100 lb downward

Support / Base